Jneopallium OPC UA Integration

User Manual

Building safety-gated cognitive control models
for industrial processes

Version: 1.0-SNAPSHOT

License: BSD 3-Clause

Author: Dmytro Rakovskyi

# 1. Introduction

Jneopallium is a Java framework for building biologically-grounded neuron networks. The industrial module turns this framework into a multi-timescale, safety-gated, auditable controller for industrial processes — chemical plants, power grids, manufacturing lines, water treatment, HVAC. The OPC UA bridge connects that controller to any standards-compliant industrial system (PLC, SCADA, simulator, digital twin) through Eclipse Milo.

This manual explains how to install the artifact, configure the bridge, model your plant in Jneopallium primitives, and run the resulting model end to end. It assumes the reader is a Java engineer with at least basic familiarity with Maven and process control concepts (PID, setpoint, interlock).

# 2. Six rules you must internalise before writing any code

The bridge enforces six non-negotiable safety invariants. Read them, then read them again. Code that violates any of them must not pass review.

- No raw write to a field actuator from neuron output. Every write goes through the chain PlanningNeuron → SafetyGateNeuron → SafetyMode check → OperatorOverrideSignal check → OpcUaCommandOutputAggregator. The aggregator rejects any ActuatorCommandSignal whose execute=false or whose loop is in shadow mode.

- Interlocks have direct authority. When InterlockSignal.tripped == true, the aggregator writes the loop to its fail-safe value regardless of anything else in the same tick. This is the only permitted bypass.

- Operator override wins for regulatory control. While an OperatorOverrideSignal is active for a tag, no neuron-derived setpoint is applied to that tag. Override does not cancel an interlock.

- Every write produces an audit record — accepted, suppressed, clamped, rate-limited, or rejected. Audits are written to a local JSONL file and, optionally, mirrored to an OPC UA audit node.

- Quality propagates. A MeasurementSignal derived from a DataValue whose StatusCode is not good() is emitted with Quality.UNCERTAIN or Quality.BAD — never silently promoted to GOOD.

- Wall-clock timestamps come from the OPC UA server, not the bridge JVM. The mapper uses sourceTimestamp, falls back to serverTimestamp, and only resorts to local time if both are null.

# 3. Prerequisites

- JDK 17 or later. The bridge uses Java records and sealed interfaces.

- Maven 3.9 or later.

- Network access to your OPC UA server. For first-run smoke tests, the public Milo demo server at opc.tcp://milo.digitalpetri.com:62541/milo is sufficient.

- For secured connections: a PKI directory containing the bridge's keypair and the trusted server certificates.

# 4. Adding Jneopallium to your project

The artifact is published to the GitLab package registry attached to project rakovpublic/jneopallium (project ID 44434192).

## 4.1 Repository declaration

Add the GitLab Maven repository to your pom.xml:

<repositories> <repository> <id>gitlab-maven</id> <url>https://gitlab.com/api/v4/projects/44434192/packages/maven</url> </repository> </repositories>

If you also want to publish derivative artifacts to the same registry, add the matching <distributionManagement> block:

<distributionManagement> <repository> <id>gitlab-maven</id> <url>https://gitlab.com/api/v4/projects/44434192/packages/maven</url> </repository> <snapshotRepository> <id>gitlab-maven</id> <url>https://gitlab.com/api/v4/projects/44434192/packages/maven</url> </snapshotRepository> </distributionManagement>

## 4.2 Authentication

Public reads of this registry do not require a token. If your network blocks anonymous GitLab API access, configure a Personal Access Token (PAT) with read_api scope in your ~/.m2/settings.xml:

<servers> <server> <id>gitlab-maven</id> <configuration> <httpHeaders> <property> <name>Private-Token</name> <value>${env.GITLAB_TOKEN}</value> </property> </httpHeaders> </configuration> </server> </servers>

Then export GITLAB_TOKEN in your shell before running Maven.

## 4.3 Dependency declaration

Add the worker artifact (which contains the OPC UA bridge, all industrial signals, and all industrial neurons):

<dependency> <groupId>com.rakovpublic.jneopallium</groupId> <artifactId>worker</artifactId> <version>1.0-SNAPSHOT</version> </dependency>

This single dependency transitively pulls in Eclipse Milo 1.1.1, Jackson, Log4j, and the rest. Verify the resolution:

mvn dependency:tree -Dincludes=org.eclipse.milo,com.rakovpublic.jneopallium

You should see milo-sdk-client:1.1.1 and worker:1.0-SNAPSHOT in the output.

# 5. Architectural overview

┌─────────────────────┐ subscriptions ┌──────────────────────────────┐ │ OPC UA server │ ───────────────────▶ │ MiloOpcUaClientService │ │ (PLC / SCADA / │ │ • OpcUaClient + transport │ │ simulator) │ ◀─────────────────── │ • OpcUaSubscription │ └─────────────────────┘ writeValues() │ • latest-value cache │ │ • alarm queue │ └──────┬──────────────┬────────┘ │ │ ┌─────────────────▼─┐ ┌─────────▼───────┐ │ OpcUaMeasurement │ │ OpcUaAlarmInput │ │ Input │ │ │ │ → IInputSignal │ │ → IInputSignal │ └─────────────────┬─┘ └─────────┬───────┘ │ │ ▼ ▼ ┌─────────────────────────────────────────┐ │ Existing Jneopallium pipeline: │ │ Sensor → MeasurementValidator → PID → │ │ Cascade → MPCPlanning → SafetyGate → │ │ Actuator │ └────────────────┬────────────────────────┘ │ List<IResult> ▼ ┌─────────────────────────────────────────┐ │ OpcUaCommandOutputAggregator │ │ 1. tripped Interlocks → fail-safe write│ │ 2. record OperatorOverride entries │ │ 3. for each Setpoint/Actuator command: │ │ INTERLOCK_HOLD? → reject + audit │ │ OVERRIDE active? → hold + audit │ │ SHADOW mode? → audit only │ │ ADVISORY mode? → require execute │ │ clamp [min,max] │ │ rate-limit by rampRateMaxPerSec │ │ diff-suppress < ε for < 5 s │ │ writeValues() → audit verdict │ └────────────────┬────────────────────────┘ │ ▼ ┌─────────────────────────────────────────┐ │ OpcUaTransparencyLogOutput │ │ local JSONL + optional OPC UA mirror │ └─────────────────────────────────────────┘

The bridge introduces three boundary classes — one for connection, one or more for input, one for output — and never modifies the neuron-network core. Every existing safety primitive (SafetyGateNeuron, InterlockNeuron, ActuatorNeuron, OperatorOverrideProcessor) keeps working unchanged.

# 6. Bridge configuration

Configuration is YAML, loaded once at startup. Hot-reload is deliberately not supported — config changes follow a Management of Change procedure that mandates a controlled restart.

## 6.1 Schema

The configuration file has six top-level sections:

- connection — endpoint URL, application identity, timeouts.

- security — security policy, message security mode, credentials.

- reads — list of OPC UA nodes to subscribe to as MeasurementSignal sources.

- writes — list of OPC UA nodes the aggregator may write to.

- alarms — list of OPC UA nodes to subscribe to as AlarmSignal sources.

- audit — local audit file path, optional OPC UA audit node, rejection policy.

- perLoopSafetyMode — per-loop SHADOW / ADVISORY / AUTONOMOUS overrides.

- tickInterval — subscription publishing interval (ISO-8601 duration).

## 6.2 Minimal example — anonymous, unsecured, read-only

This is appropriate for a smoke test against the public Milo demo server.

connection: endpointUrl: "opc.tcp://milo.digitalpetri.com:62541/milo" applicationName: "Jneopallium-OPCUA-Bridge" applicationUri: "urn:rakovpublic:jneopallium:bridge:dev01" requestTimeout: "PT5S" sessionTimeout: "PT2M" keepAliveFailuresAllowed: 3 security: policy: NONE mode: NONE auth: type: "Anonymous" reads: - loopId: "DEMO-CLOCK" nodeId: "i=2258" signalTag: "DEMO.CLOCK.UTC" direction: READ writes: [] alarms: [] audit: localAuditFile: "/tmp/jneopallium-opcua-audit.jsonl" writeRejectedToAudit: true tickInterval: "PT0.25S"

## 6.3 Production example — secured, with writes

connection: endpointUrl: "opc.tcp://plant.local:4840" applicationName: "Jneopallium-OPCUA-Bridge" applicationUri: "urn:rakovpublic:jneopallium:bridge:plant01" requestTimeout: "PT5S" sessionTimeout: "PT2M" keepAliveFailuresAllowed: 3 security: policy: BASIC256SHA256 mode: SIGN_AND_ENCRYPT pkiDir: "/var/lib/jneopallium/opcua-pki" certAlias: "bridge-cert" certPassword: "${OPCUA_CERT_PASSWORD}" auth: type: "UsernamePassword" username: "plant-bridge" passwordEnv: "OPCUA_USER_PASSWORD" reads: - loopId: "TIC-101" nodeId: "ns=2;s=Plant.Temperature" signalTag: "PLANT.TIC101.PV" direction: READ - loopId: "PIC-102" nodeId: "ns=2;s=Plant.Pressure" signalTag: "PLANT.PIC102.PV" direction: READ - loopId: "FIC-101" nodeId: "ns=2;s=Plant.MotorSpeed" signalTag: "PLANT.FIC101.PV" direction: READ writes: - loopId: "FIC-101" nodeId: "ns=2;s=Plant.TargetMotorSpeed" signalTag: "PLANT.FIC101.SP" direction: WRITE failSafeValue: 0.0 rampRateMaxPerSec: 5.0 minClampValue: 0.0 maxClampValue: 100.0 alarms: - loopId: "PLANT-ALARMS" nodeId: "ns=2;s=Plant.Alarm" signalTag: "PLANT.ALARM" direction: READ audit: localAuditFile: "/var/log/jneopallium/opcua-audit.jsonl" opcUaAuditNodeId: "ns=2;s=Plant.JneopalliumAuditLog" writeRejectedToAudit: true perLoopSafetyMode: TIC-101: SHADOW PIC-102: SHADOW FIC-101: ADVISORY tickInterval: "PT0.25S"

## 6.4 Field reference

The following table summarises the meaning and defaults of every field. All durations are ISO-8601 (PT5S = 5 seconds, PT2M = 2 minutes).

| Field | Type | Required | Default | Notes |
| --- | --- | --- | --- | --- |
| connection.endpointUrl | string | yes | — | Begins with opc.tcp://. |
| connection.applicationName | string | no | Jneopallium-OPCUA-Bridge | Shown in the server's session list. |
| connection.applicationUri | string | no | urn:rakovpublic:jneopallium:bridge | Must be unique per deployment. |
| connection.requestTimeout | duration | no | PT5S | Per-request transport timeout. |
| connection.sessionTimeout | duration | no | PT2M | Server-side session lifetime. |
| connection.keepAliveFailuresAllowed | int | no | 3 | Channel reconnect threshold. |
| security.policy | enum | no | NONE | NONE / BASIC256SHA256 / AES128_SHA256_RSAOAEP / AES256_SHA256_RSAPSS. |
| security.mode | enum | no | NONE | NONE / SIGN / SIGN_AND_ENCRYPT. |
| security.auth.type | enum | no | Anonymous | Anonymous / UsernamePassword / X509. |
| security.auth.passwordEnv | string | for UP | — | Name of the environment variable that contains the password. The password itself never appears in YAML. |
| reads[].loopId | string | yes | — | Logical loop name. Used in audit and per-loop safety mode lookup. |
| reads[].nodeId | string | yes | — | OPC UA node id, e.g. ns=2;s=Plant.Temperature or i=2258. |
| reads[].signalTag | string | yes | — | ISA-95-style tag emitted on signals, e.g. PLANT.TIC101.PV. |
| writes[].failSafeValue | double | no | null | Value written on interlock trip. |
| writes[].rampRateMaxPerSec | double | no | null | Maximum change per second; commands above this are rate-limited and audited as such. |
| writes[].minClampValue / maxClampValue | double | no | null | Hard clamp range. |
| audit.localAuditFile | string | yes | — | Append-only JSONL. The bridge creates parent directories if missing. |
| audit.opcUaAuditNodeId | string | no | null | Optional OPC UA node where audit lines are also mirrored as JSON strings. |
| audit.writeRejectedToAudit | bool | no | false | When false, REJECTED entries are dropped to reduce noise. |
| perLoopSafetyMode | map | no | empty | Per-loop SHADOW / ADVISORY / AUTONOMOUS. Loops not listed are treated per the global IndustrialConfig. |
| tickInterval | duration | no | PT0.25S | Subscription publishing interval. Floor is 50 ms. |

# 7. Wiring the bridge — minimal Java program

The bridge has three classes you instantiate explicitly and three implementations of existing Jneopallium contracts (IInitInput, IOutputAggregator) you register on your network. The example below brings them all up against the public Milo demo server.

import com.fasterxml.jackson.databind.ObjectMapper; import com.fasterxml.jackson.dataformat.yaml.YAMLFactory; import com.fasterxml.jackson.datatype.jsr310.JavaTimeModule; import com.rakovpublic.jneuropallium.worker.input.opcua.OpcUaAlarmInput; import com.rakovpublic.jneuropallium.worker.input.opcua.OpcUaMeasurementInput; import com.rakovpublic.jneuropallium.worker.net.neuron.impl.industrial.opcua.MiloOpcUaClientService; import com.rakovpublic.jneuropallium.worker.net.neuron.impl.industrial.opcua.OpcUaBridgeConfig; import com.rakovpublic.jneuropallium.worker.net.neuron.impl.industrial.opcua.OpcUaNodeBinding; import com.rakovpublic.jneuropallium.worker.output.opcua.OpcUaCommandOutputAggregator; import com.rakovpublic.jneuropallium.worker.output.opcua.OpcUaTransparencyLogOutput; import java.nio.file.Path; import java.util.List; public final class BridgeBootstrap { public static void main(String[] args) throws Exception { // 1. Load YAML var mapper = new ObjectMapper(new YAMLFactory()).registerModule(new JavaTimeModule()); OpcUaBridgeConfig cfg = mapper.readValue( Path.of(args[0]).toFile(), OpcUaBridgeConfig.class); // 2. Connection lifecycle try (MiloOpcUaClientService svc = new MiloOpcUaClientService(cfg); OpcUaTransparencyLogOutput audit = new OpcUaTransparencyLogOutput(cfg.audit(), svc)) { // 3. Resolve bindings now that the service has registered them List<OpcUaNodeBinding> readBindings = cfg.reads().stream() .map(c -> svc.bindingBySignalTag(c.signalTag())) .toList(); List<OpcUaNodeBinding> alarmBindings = cfg.alarms().stream() .map(c -> svc.bindingBySignalTag(c.signalTag())) .toList(); // 4. Inputs and output aggregator var measurements = new OpcUaMeasurementInput("opcua.measurements", null, svc, readBindings); var alarms = new OpcUaAlarmInput("opcua.alarms", null, svc, alarmBindings); var commands = new OpcUaCommandOutputAggregator(cfg, svc, audit); // 5. Register on your existing Jneopallium network: // network.addInputSource(measurements); // network.addInputSource(alarms); // network.addOutputAggregator(commands); // network.run(); // For a smoke test, just sleep and check the latest-value cache: Thread.sleep(2_000); System.out.println("Latest UTC = " + svc.latest("DEMO.CLOCK.UTC")); } } }

A few invariants to internalise:

- MiloOpcUaClientService and OpcUaTransparencyLogOutput are AutoCloseable. Always wrap them in try-with-resources. Failing to close the service leaks a TCP connection and a Milo subscription on the server.

- The OpcUaNodeBinding instances are looked up after the service registers them. Do not construct OpcUaNodeBinding yourself for read paths.

- null for the second argument to OpcUaMeasurementInput selects the default MeasurementSignal.PROCESSING_FREQUENCY (loop=1, epoch=1). Pass an explicit ProcessingFrequency if you want a slower loop for slow process variables.

# 8. Modelling a plant in Jneopallium primitives

A Jneopallium model of an industrial process is built in three stages: define the signals carried on the wire, place the neurons that process them, and wire the input and output boundaries. The OPC UA bridge supplies the boundary; the neurons and signals already exist in the industrial package.

## 8.1 Industrial signals

| Signal | Loop / Epoch | Payload |
| --- | --- | --- |
| MeasurementSignal | 1 / 1 | tag, value, Quality, wall-clock ms |
| SetpointSignal | 1 / 2 | tag, setpoint, ramp rate, source |
| ActuatorCommandSignal | 1 / 1 | tag, target / current, execute |
| AlarmSignal | 1 / 1 | AlarmPriority, tag, condition, ts |
| InterlockSignal | 1 / 1 | id, tripped, causes |
| DegradationSignal | 2 / 3 | asset id, RUL hours, confidence |
| EfficiencySignal | 2 / 1 | unit id, efficiency, baseline |
| BatchStateSignal | 2 / 2 | batch id, BatchPhase, key metrics |
| OperatorOverrideSignal | 1 / 1 | tag, OverrideKind, operator, reason, manual value |
| MaintenanceWindowSignal | 2 / 10 | asset id, scheduled tick, duration |

The Loop / Epoch column reflects the industrial multi-timescale design: regulatory control runs at loop 1, supervisory and slow loops at loop 2, with relative epoch ratios chosen to match physical timescales.

## 8.2 Industrial neurons (by layer)

- Layer 0 (field I/O): SensorNeuron, MeasurementValidatorNeuron.

- Layer 1 (regulatory): PIDNeuron, CascadeNeuron, FeedForwardNeuron.

- Layer 2 (supervisory): SetpointOptimiserNeuron, AlarmAggregationNeuron, ModeControllerNeuron.

- Layer 3 (model and memory): ProcessModelNeuron, DegradationModelNeuron, ProductQualityModelNeuron.

- Layer 4 (planning): MPCPlanningNeuron, CampaignPlanningNeuron, MaintenanceSchedulingNeuron.

- Layer 5 (action): SafetyGateNeuron, ActuatorNeuron, InterlockNeuron.

- Layer 7 (homeostasis): OscillationMonitorNeuron, EnergyAccountingNeuron.

Every concrete neuron has a matching I*Neuron interface; processors target the interface, never the concrete type, so a deployment can swap a PID for an MPC without touching processors.

## 8.3 Worked example — a single temperature loop

The simplest non-trivial model is a single temperature control loop. The OPC UA server exposes the process variable on ns=2;s=Plant.Temperature and the manipulated variable on ns=2;s=Plant.HeaterSetpoint. The plant alarm node lives at ns=2;s=Plant.Alarm.

Step 1 — bridge YAML. Bind the three nodes:

reads: - { loopId: "TIC-101", nodeId: "ns=2;s=Plant.Temperature", signalTag: "PLANT.TIC101.PV", direction: READ } writes: - { loopId: "TIC-101", nodeId: "ns=2;s=Plant.HeaterSetpoint", signalTag: "PLANT.TIC101.SP", direction: WRITE, failSafeValue: 0.0, rampRateMaxPerSec: 2.0, minClampValue: 0.0, maxClampValue: 100.0 } alarms: - { loopId: "PLANT-ALARMS", nodeId: "ns=2;s=Plant.Alarm", signalTag: "PLANT.ALARM", direction: READ } perLoopSafetyMode: TIC-101: SHADOW # start in SHADOW; observe; then ADVISORY; only then AUTONOMOUS.

Step 2 — neuron placement.

- Layer 0: a SensorNeuron for PLANT.TIC101.PV and a MeasurementValidatorNeuron to flag out-of-range or stuck values.

- Layer 1: one PIDNeuron configured for the loop's gains and a target setpoint.

- Layer 2: AlarmAggregationNeuron to suppress chattering and ModeControllerNeuron to route through the plant state machine.

- Layer 4: optionally an MPCPlanningNeuron if you want predictive setpoints.

- Layer 5: SafetyGateNeuron for the loop, ActuatorNeuron to dispatch, and InterlockNeuron for the high-temperature interlock.

- Layer 7: OscillationMonitorNeuron watching the PV and flagging oscillation severity for the safety gate to consider.

Step 3 — interlocks. Construct the InterlockNeuron with one rule — "temperature above 95 °C trips the heater to fail-safe (0)". Call seal() on the neuron at construction time. Subsequent additions throw IllegalStateException. This implements the architectural rule that the SRS is compiled once.

Step 4 — operator override path. The user interface that lets an operator put TIC-101 into MANUAL emits an OperatorOverrideSignal(tag="PLANT.TIC101.SP", kind=MANUAL, operatorId="op42", reason="manual hold", manualValue=42.0). The aggregator's OverrideRegistry records the override; until it expires, no neuron-derived setpoint reaches PLANT.TIC101.SP.

Step 5 — start in SHADOW. Run the network for at least one full shift in SHADOW mode. The bridge writes nothing. The audit file fills with what the network would have written. Compare against operator decisions; if the agreement rate is acceptable, promote TIC-101 to ADVISORY. Only after a documented period of advisory operation should you promote to AUTONOMOUS.

This is the canonical commissioning sequence. Skipping it is unsafe.

## 8.4 Cascaded loops

A cascaded loop (outer slow loop drives the setpoint of an inner fast loop) maps to one PIDNeuron per loop with a CascadeNeuron between them. The CascadeNeuron exposes setBroken(true), which freezes the inner setpoint at its last-good value — the standard recovery action when the outer loop is suspect. The OscillationMonitorNeuron's BREAK_CONNECTION intervention triggers exactly this state.

## 8.5 Safety mode lifecycle

Per-loop safety mode is the central dial during commissioning:

- `SHADOW` — the aggregator records what it would write but performs no field write. Use during initial commissioning, after model changes, and after sensor replacements.

- `ADVISORY` — the aggregator passes the value to the operator's HMI for confirmation. Used while building operator trust.

- `AUTONOMOUS` — the aggregator writes after the harm gate clears. Reserved for well-characterised, low-consequence loops.

A plant can run 90% of loops AUTONOMOUS, 9% ADVISORY, and 1% SHADOW simultaneously. There is no "global mode" that overrides per-loop mode for regulatory writes — IndustrialConfig.safetyMode is the default for loops not listed in perLoopSafetyMode.

# 9. Audit log format

Every record is one JSON object on its own line, in the order the bridge emits them. Keys are stable and intended for ingestion by a SIEM or historian.

{ "ts": 1740000000000, "run": 12345, "verdict": "APPLIED", "loopId": "FIC-101", "tag": "PLANT.FIC101.SP", "proposed": 47.3, "effective": 45.0, "reason": "RATE_LIMITED", "safetyMode": "AUTONOMOUS" }

verdict values:

- APPLIED — write succeeded at the OPC UA layer.

- REJECTED — the aggregator refused the write. reason carries the cause (UNKNOWN_TAG, INTERLOCK_HOLD, OVERRIDE_HOLD, SHADOW_MODE, ADVISORY_HOLD, EXCEPTION:*).

- INTERLOCK_TRIP — the aggregator wrote the loop's failSafeValue because of a tripped interlock.

- OVERRIDE_HOLD — operator override is active for the tag; nothing written.

- FAILED — the OPC UA write returned a non-good status code or threw an exception.

reason values for APPLIED writes describe any modification: RATE_LIMITED, CLAMPED_HIGH, CLAMPED_LOW, DIFF_SUPPRESSED, or empty when applied verbatim.

# 10. Operating procedures

## 10.1 First-time smoke test

- Build the project: mvn -B -U clean verify.

- Drop the YAML from §6.2 at /tmp/opcua-bridge-demo.yaml.

- Run BridgeBootstrap /tmp/opcua-bridge-demo.yaml.

- Within ~2 seconds, the program prints a non-null DataValue for DEMO.CLOCK.UTC.

If it fails, run with -Dorg.slf4j.simpleLogger.defaultLogLevel=debug and inspect the Milo client log.

## 10.2 Promoting a loop from SHADOW to ADVISORY

- Run for at least one full operating shift in SHADOW.

- Process the audit file: count APPLIED (would-be) writes, group by hour, compare against operator-applied setpoints from the historian.

- If divergence is bounded and explainable, change perLoopSafetyMode.<LOOP_ID> from SHADOW to ADVISORY in YAML.

- Restart the bridge — config is not hot-reloadable.

## 10.3 Diagnosing a stuck binding

A binding that never produces a MeasurementSignal usually means one of three things:

- The OPC UA node id is wrong. Verify with the Milo BrowseExample against your server.

- The user account lacks read permission. Check the server log.

- The session is connected but the subscription failed. The bridge logs Failed to create MonitoredItem nodeId=… svc=… op=… at ERROR.

MiloOpcUaClientService.snapshotLatest() returns the latest-value cache keyed by signalTag; missing keys mean no value has yet arrived for that binding.

## 10.4 Reconnecting after a network interruption

Milo's client transparently retries the channel. The bridge does not silently replay buffered writes after reconnection — the plant state may have changed. After a long disconnect, the operator UI must reissue any setpoint that was in flight.

# 11. Regulatory posture

The bridge and industrial module are designed to align with — though not replace — the following standards:

- IEC 61508 — functional safety. The bridge does not implement SIL functions itself; SIS (safety instrumented systems) remain on certified safety PLCs, network-segregated from this bridge.

- IEC 62443 — OT cybersecurity. Use the OPC UA security policy (BASIC256SHA256 minimum) and run the bridge inside the OT network zone.

- ISA-95 / IEC 62264 — enterprise-control integration. The signalTag convention follows ISA-95 area/unit/loop notation.

- ISA-18.2 — alarm management. AlarmAggregationNeuron implements suppression and per-minute rate limiting.

- 21 CFR Part 11 — electronic records. The hash-chain-enabled audit trail (see IndustrialConfig.hashChainEnabled) provides tamper-evidence.

# 12. Out of scope

This integration deliberately does not provide:

- a replacement for certified safety PLCs;

- cloud-round-trip control (the bridge runs on-premises);

- in-loop LLM or external decision systems;

- uncontrolled model updates — model changes are versioned and reviewed through the same MoC procedure as any control change.

# 13. References

- Eclipse Milo — https://github.com/eclipse-milo/milo (version 1.1.1, February 2026).

- Jneopallium — https://github.com/rakovpublic/jneopallium.

- OPC UA Foundation, Unified Architecture — getting started: https://opcfoundation.org/unified-architecture-getting-started/.

- Rakovskyi, D. (2024). Framework for Natural Neuron Network Modeling: The Jneopallium Approach. IJSR 13(7).

- IEC 61508:2010 — Functional safety of E/E/PE safety-related systems.

- IEC 62443 — Industrial communication networks — IT security.

- ISA-95 / IEC 62264 — Enterprise-control integration.

- ISA-18.2-2016 — Alarm systems management.

- Seborg, D.E., Edgar, T.F., Mellichamp, D.A., Doyle, F.J. (2016). Process Dynamics and Control. Wiley.