JNEOPALLIUM · INDUSTRIAL LOOP GUARDIAN ARCHITECTURE ARTICLE

A Supervisory Brain for Your Plant

Cross-loop, cross-timescale diagnosis above PLC/PID/SIS — complete architecture, explained

How a brain-inspired supervisory layer turns the OPC UA and MQTT telemetry you already have into early diagnosis of pump wear, control-loop oscillation, sensor drift, and wasted energy — without ever touching your deterministic controls. Written so a non-specialist can follow every step.

| Document | Architecture & Technical Overview |
| --- | --- |
| Product | Jneopallium Industrial Loop Guardian (FMI Skid Demo) |
| Model | industrial-loop-guardian 1.0.0 + machine-health condition monitoring |
| Safety mode | ADVISORY (supervisory, recommend-only) |
| Author | Dmytro Rakovskyi — Kharkiv, Ukraine |
| Date | 23 June 2026 |
| Audience | Plant managers, controls engineers, executives, newcomers |
| License | BSD 3-Clause |

What's inside

1.  Executive summary — the one-page version

2.  The problem: why good controls still lose money

3.  The big idea: supervise, don't replace

4.  The platform underneath: the Jneopallium framework

5.  Architecture overview: how the pieces fit together

6.  The skid it supervises

7.  The protocol boundary: OPC UA, MQTT, and PLC/SIS

8.  Signals: the common language, on many clocks

9.  The four things it diagnoses

10.  Hearing and feeling the machine: multimodal condition monitoring

11.  The trained model and the deployable network

12.  Safety by design: why it cannot trip your plant

13.  Deployment topology: where it runs

14.  End-to-end walkthrough: nine scenarios

15.  Glossary for non-specialists

1  Executive summary

A good PID controller holds one variable — a temperature, a flow, a level — beautifully. But a plant rarely loses money on a single well-tuned loop. It loses money on the things that no single loop can see: a pump quietly wearing out, a control loop slowly drifting out of tune, a temperature sensor creeping off-calibration, and a combination of controllers that each behave correctly while together burning more energy than they should.

The Jneopallium Industrial Loop Guardian is a supervisory layer that sits above your PLC, PID, and safety systems — never instead of them. It reads the OPC UA and MQTT telemetry you already produce, correlates signals across many timescales (milliseconds to weeks), and emits a single, evidenced advisory: what is happening, why, how urgent it is, and what it is worth in money. It never blocks, never trips, never overrides a safety interlock.

The one sentence to remember Your PLC/PID/SIS keeps doing the fast, deterministic control and hard safety. The Loop Guardian adds cross-loop, cross-timescale operational intelligence on top — diagnosis, energy optimisation, and maintenance planning — and only ever recommends.

Its design is borrowed from the brain: fast reflexes and slow judgement running at the same time, with specialised "neurons" that combine signals other tools look at in isolation. The result is a product that is easy to trust — it runs in ADVISORY mode, keeps every deterministic control authoritative, and explains every recommendation.

2  The problem: why good controls still lose money

A single loop is not where the money leaks

Classic controls and threshold alarms look at one variable at a time. That is exactly right for fast, stable regulation — and exactly wrong for the expensive, slow-moving problems:

Hidden degradation. A bearing wears over weeks. "Bearing temperature > 85 °C → alarm" fires only at the end — after the damage. The early evidence is spread across vibration, suction pressure, power-per-unit-flow, and running hours, on different clocks.

Cross-loop waste. A heater raises temperature while a cooling valve removes heat while a pump runs faster than needed. Each local controller is "correct"; the combination wastes energy no single loop can detect.

Nuisance alarms. The same rising temperature is normal at startup and alarming in steady state. Context-free thresholds either over-alarm or miss the real event.

Sensor-fault ambiguity. Is the process actually getting hotter, or is one sensor drifting? Majority voting cannot tell; the answer needs the physical model, the actuator commands, and the maintenance history together.

What that costs

Unplanned shutdowns, unnecessary preventive maintenance, shortened equipment life, and quietly elevated energy bills. Every one of these is a decision that depends on several signals evolving over different timescales — precisely the case where a supervisory, multi-timescale architecture earns its keep, and a single PID loop cannot.

3  The big idea: supervise, don't replace

The commercially credible — and safe — design is a hybrid. Keep what already works; add what it cannot do:

PLC / PID / SIS +-- deterministic millisecond control and hard safety (unchanged) Jneopallium Industrial Loop Guardian (supervisory, above) +-- multi-loop coordination +-- oscillation and sensor-fault diagnosis +-- energy optimisation +-- degradation prediction and maintenance planning +-- bounded setpoint recommendations (advisory)

A PID controller usually beats a sophisticated AI on cost, predictability, validation effort, and reliability when controlling one stable variable. So we do not compete there. The Loop Guardian becomes valuable only when a decision depends on many signals over many timescales — diagnosis, economic ranking, and planning.

Where it does and does not help High value: predictive maintenance, oscillation diagnosis, sensor-drift discrimination, energy and setpoint optimisation, batch-context anomaly detection. Low or no value: a single stable regulatory loop, and hard interlocks / emergency shutdown — which must remain deterministic. The product is designed to respect that line.

4  The platform underneath: the Jneopallium framework

The Loop Guardian is one application of Jneopallium, a Java framework for building biologically-grounded neuron networks (published in the *International Journal of Science and Research*, 2024). Three of its ideas explain why it is good at supervisory work.

1. Typed signals — meaning, not just numbers

A flow measurement, a vibration reading, a maintenance work-order, and an energy meter are *different kinds of signal* with different meaning and urgency. The engine routes each to the right specialist and keeps the evidence intact all the way to the advisory.

2. Many clocks — fast reflexes, slow judgement

Biology runs on many clocks at once. Jneopallium copies this: fast signals (measurements, commands, interlocks) are processed every loop; slower context (degradation, efficiency, maintenance windows) is processed every 10 to 60 loops. A pump-health neuron can weigh instantaneous hydraulics against a multi-week wear trend in one coherent judgement.

| Signal | Cadence | Function |
| --- | --- | --- |
| Flow, pressure, interlocks | Every tick | Immediate hydraulic condition and safety state |
| Pump command vs. actual speed | Every tick | Actuator tracking |
| Vibration RMS | Every 5–10 ticks | Mechanical anomaly |
| Bearing temperature, power | Every 10 ticks | Thermal/mechanical condition, efficiency |
| Production load | Every ~50 ticks | Operating context |
| Degradation estimate | Hundreds of ticks | Long-term health |
| Maintenance schedule | Thousands of ticks | Planning context |

3. Stateless, swappable specialists

Each processing step is a small, stateless processor wired to a neuron through an interface. Any detector can be upgraded or replaced for a particular site without touching the rest — a lab runs a simple model; a refinery plugs in a richer one behind the same interface.

5  Architecture overview: how the pieces fit together

Telemetry flows one way through increasingly intelligent stages; an auditable advisory flows out the other end:

FMI skid / OPC UA / MQTT / Kafka telemetry -> fast telemetry validation and loop state -> trained diagnostic finding heads -> economic advisory planning + fixed safety gate -> industrial advisory JSONL (asset, finding, confidence, economic basis)

The trained network is five layers of seventeen real neurons:

| Layer | Size | Job, in plain language |
| --- | --- | --- |
| 0 — Input | — | Plant + supervisory-context boundary (OPC UA, MQTT, FMI replay, Kafka) |
| 1 — Fast telemetry | 7 | Validate measurements, track interlocks, override, fast loop state |
| 2 — Diagnostic heads | 4 | Trained detectors: pump wear, oscillation, sensor drift, energy |
| 3 — Advisory planning | 4 | Maintenance scheduling, bounded trim, economic basis, safety gate |
| 4 — Result | 2 | Emit maintenance and energy advisories as JSONL |

6  The skid it supervises

The demo runs a deterministic heated circulation and heat-exchanger skid, simulated with an FMI 2.0 Co-Simulation FMU and driven through a real protocol gateway. It is rich enough to be a commercially testable prototype — it models the physics where the money actually leaks:

Process and measured temperature, circulation flow, suction pressure.

Pump speed and power, cooling-valve position, heater power.

Vibration RMS and bearing temperature (the wear signals).

Injectable faults: valve sticking, pump wear, temperature-sensor drift, thermal runaway.

Deterministic local interlocks: high temperature, low flow, low suction pressure.

The model includes tank thermal inertia, pump and valve lag, pump-flow and power curves, vibration and bearing-temperature wear effects, and sensor drift/noise — so the diagnostic heads learn from realistic, physically coupled behaviour rather than a flat table.

7  The protocol boundary: OPC UA, MQTT, and PLC/SIS

OPC UA and MQTT are complementary, and the demo keeps a strict, commercially sensible boundary:

| Path | Role | Authority |
| --- | --- | --- |
| PLC / PID / SIS | Hard real-time control and interlocks | Always authoritative |
| OPC UA | Bounded local actuator command path | Only command path; tightly limited |
| MQTT | Telemetry and advisory distribution | Never actuates (AUTONOMOUS rejected) |

There are exactly three OPC UA command nodes (cooling valve, pump speed, heater power), and the Java MqttBridgeConfig constructor structurally rejects an AUTONOMOUS mode — MQTT carries vibration, energy, status, and advisories, but its tags never match an actuator command tag. When a command is issued, it passes a fixed priority chain before any write happens:

hard interlock -> local fail-safe -> operator override -> safety mode -> validation/quality -> clamp -> ramp limit -> diff suppression -> OPC UA write -> audit

| Command | Fail-safe default |
| --- | --- |
| Cooling valve | 100% open (maximum cooling) |
| Pump speed | 30% |
| Heater power | 0% (off) |

8  Signals: the common language, on many clocks

Everything the system sees becomes a typed industrial signal. Each declares how often it should be processed, realising the "many clocks" idea concretely:

| Signal | Carries | Cadence (loop) |
| --- | --- | --- |
| MeasurementSignal | Process measurements (temp, flow, pressure…) | Every loop |
| AlarmSignal | Plant alarms | Every loop |
| InterlockSignal | Hard interlock state | Every loop |
| OperatorOverrideSignal | Operator manual control | Every loop |
| ActuatorCommandSignal | Bounded actuator command | Every loop |
| DegradationSignal | Equipment degradation evidence | Every 10 loops |
| EfficiencySignal | Energy / efficiency context | Every 10 loops |
| SetpointSignal | Bounded setpoint recommendation | Every 10 loops |
| MaintenanceWindowSignal | Planned-maintenance context | Every 60 loops |
| MachineWaveformSignal | Raw acoustic / vibration waveform | Every loop |
| MachineFeatureSignal | Acoustic & vibration features | Every ~4 loops |
| MachineHealthAdvisorySignal | Health score + fault probabilities | Every ~10 loops |

Fast signals give immediate condition and safety state; slow signals carry the context that *changes the meaning* of the fast ones — without ever slowing the fast path down.

9  The four things it diagnoses

The trained layer holds four diagnostic finding heads — narrow, high-value detectors. Each leans on a coherent set of evidence (shown here in plain language, drawn from the model's learned weights):

1 · Pump wear and cavitation risk

Rising vibration and bearing temperature, increasing pump power, and low suction pressure / low flow point to wear or cavitation — distinguished from a mere temporary high load by the *combination* and its trend.

2 · Control-loop oscillation and tuning degradation

A valve-stiction proxy (command moves, position lags), actuator reversal density, and load-transition patterns separate genuine tuning degradation from normal transients.

3 · Temperature-sensor drift

A physical temperature model produces a residual; a large, persistent residual with no matching power or process response means the sensor is drifting, not the process — avoiding an unnecessary shutdown.

4 · Energy-per-unit-production deterioration

Energy consumption relative to production, combined with health risk and actuator activity, flags a loop that holds its variable correctly while quietly wasting energy.

10  Hearing and feeling the machine: multimodal condition monitoring

The four heads above read *process* telemetry. The updated Guardian adds a multimodal machine-health subsystem that also *hears and feels* the equipment — acoustic and vibration condition monitoring — implemented as a read-only / shadow / advisory runtime layer that never touches control. It turns raw sound and vibration into named fault hypotheses with a calibrated health score and an honest measure of its own uncertainty:

| Stage (owning neuron) | What it does |
| --- | --- |
| Acoustic features (AcousticFeatureNeuron) | RMS, crest factor, spectral centroid from the sound stream |
| Vibration features (VibrationFeatureNeuron) | RMS, envelope energy, crest factor from the vibration stream |
| Operating regime (OperatingRegimeNeuron) | Speed-normalised scoring so a reading means the right thing at each load |
| Baseline & domain shift (MachineBaselineNeuron) | Per-machine baseline, a domain-shift score, cross-sensor consistency |
| Fault hypotheses (FaultHypothesisNeuron) | Probabilities for bearing damage, cavitation, imbalance, sensor fault, unknown anomaly |
| Health correlation & gate (MachineHealthCorrelationNeuron, AdvisoryGateNeuron) | Fuses the evidence into a health advisory and keeps it advisory-only |

The health advisory carries a healthScore, an anomalyProbability, per-fault faultProbabilities (bearing damage, cavitation, imbalance, sensor fault), an unknownAnomalyProbability, a domainShiftScore, and an uncertainty value — so it tells you not just *what* it suspects but *how sure it is*.

Why domain-shift and uncertainty matter A condition-monitoring model that confidently mislabels an unfamiliar machine is dangerous. This subsystem reports a domain-shift score and an uncertainty value, so an unfamiliar machine or regime surfaces as "I am not sure" rather than a false alarm — exactly what makes it trustworthy in shadow mode.

It is trained on public machine-condition datasets — MIMII, DCASE machine-condition, MIMII DUE/DG, and the Paderborn Bearing Data Center — plus the FMI pump simulator and authorised site telemetry, and it is read-only by construction: the MachineHealthAdvisorySignal never writes an actuator command, and the interlocks, safety gate, and operator override remain authoritative.

11  The trained model and the deployable network

Bundled with the product is a checked-in reference model, industrial-loop-guardian. Training does not stop at a set of weights — it emits a complete, deployable JNeopallium network: five layers, seventeen real neurons, 39 features, 156 trainable weights and 4 biases, written into ready-to-load layer-configuration files that reference concrete runtime classes.

| Generated layer | Real neurons / role |
| --- | --- |
| Fast telemetry | SensorNeuron, MeasurementValidatorNeuron, OscillationMonitorNeuron, … |
| Diagnostic heads | DegradationModelNeuron, EnergyAccountingNeuron (the four finding heads) |
| Advisory planning | MaintenanceSchedulingNeuron, SetpointOptimiserNeuron, EconomicBasisNeuron, SafetyGateNeuron |
| Machine-health runtime (Java) | AcousticFeatureNeuron, VibrationFeatureNeuron, FaultHypothesisNeuron, MachineHealthCorrelationNeuron, AdvisoryGateNeuron |
| Result | Advisory JSONL output neurons |

Each diagnostic head also records a logical role (e.g. PumpHealthAndEfficiencyNeuron, OscillationDiagnosisNeuron, SensorFaultDiscriminationNeuron, EconomicBasisNeuron, SafetyEnvelopeNeuron), the features it is allowed to use (featureGate), and its ownedReasoning — so a production reviewer can see that the logic is encapsulated inside the Jneopallium model, not hidden in glue code.

Read this honestly On the bundled, deterministic reference skid the model scores near-perfectly (macro-F1 ≈ 0.9995, and only a handful of energy-head false positives out of thousands). That demonstrates the pipeline and the diagnostic separation — it is NOT a claim of real-world accuracy, which must be earned on external historian, CMMS, and energy-meter data. The Test Report states this plainly.

12  Safety by design: why it cannot trip your plant

1.  Supervisory and advisory by default. The safety ceiling is ADVISORY. The Loop Guardian recommends; it does not control. Bounded autonomous setpoint changes require a separate, deliberately added safety case, approval workflow, and rollback path.

2.  Deterministic controls stay authoritative. PLC/PID/SIS own fast control and hard safety. Hard interlocks, local fail-safe logic, and operator overrides take priority over anything the model suggests — structurally, in the command priority chain.

3.  MQTT cannot actuate. The telemetry/advisory path is structurally barred from autonomous action; only the bounded OPC UA path can command, and only within clamps and ramp limits.

4.  Fail-safe on loss. On OPC UA loss the skid applies local fail-safe values; on MQTT loss fast-loop control availability stays at 1.0. Losing the supervisor never endangers the plant.

And every advisory carries its economic basis and a safety-envelope result, so an engineer can see not just *what* is recommended but *why*, *what it is worth*, and *that it stays inside the configured envelope*.

13  Deployment topology: where it runs

| Mode | Description | Typical use |
| --- | --- | --- |
| Local | Single Java process | Offline replay, pilots, edge box at the plant |
| Cluster (HTTP) | Distributed over HTTP | Multi-asset, multi-line sites |
| Cluster (gRPC) | Distributed over gRPC; FPGA-capable | High-throughput fleets |

Telemetry arrives through bridges that translate a protocol into typed signals: OPC UA measurement/alarm inputs, MQTT telemetry inputs, FMI and PLC4X measurement/event inputs, and a Kafka shadow stream — plus a machine-waveform input for the acoustic/vibration streams. A site-specific input adapter converts your historian or live feeds into the same typed signals while preserving event time, so the same model runs on a laptop replay and a clustered plant alike.

14  End-to-end walkthrough: nine scenarios

The deterministic runner exercises nine scenarios and records evidence for each. A few show the architecture's character:

pump-wear — degradation evidence accumulates; the pump-health head raises a maintenance advisory with an economic basis (fault evidence appears ~58 s into the run).

oscillation — the oscillation head separates tuning degradation from normal load transitions.

temperature-sensor-drift — the sensor-drift head attributes the anomaly to the sensor, not the process, avoiding a needless trip.

high-temperature-interlock — the hard interlock writes cooling and heater fail-safe; interlock latency is ~0.1 s, owned by the deterministic layer, not the model.

mqtt-outage — fast-loop control availability stays at 1.0; advisories pause, control does not.

opcua-outage — local fail-safe values are applied; the plant stays safe without the supervisor.

The point of the scenarios In every case the model adds diagnosis and economic context, while the deterministic controls keep the plant safe and running. The supervisor improves the decision; it never owns the safety.

15  Glossary for non-specialists

| Term | Plain-language meaning |
| --- | --- |
| Advisory mode | The system recommends; humans and PLCs decide. It never trips the plant. |
| Condition monitoring | Judging machine health from sound and vibration, not just process values. |
| Domain shift | When live data differs from the training data — the model flags this instead of guessing. |
| Cavitation | Vapour bubbles forming at a pump's suction, damaging it — caused by low pressure. |
| Interlock | A hard, deterministic safety rule (e.g. high temp → cooling fail-safe). |
| FMI / FMU | A standard way to package a plant simulation; used here to drive the demo skid. |
| OPC UA | An industrial information/communication standard; here, the bounded command path. |
| MQTT | A lightweight publish/subscribe protocol; here, telemetry and advisories only. |
| PLC / PID / SIS | The deterministic controllers and safety system that own fast control. |
| Setpoint | The target value a controller aims for (e.g. desired temperature). |
| Stiction | Static friction in a valve that makes its position lag its command. |
| Supervisory layer | A layer that reasons across loops and timescales, above the controllers. |
| Economic basis | The money value the system attaches to a finding (e.g. avoided shutdown). |

Jneopallium Industrial Loop Guardian · FMI Skid Demo. Architecture article for technical and non-technical readers. Supervisory above PLC/PID/SIS. Safety mode: ADVISORY. License: BSD 3-Clause.