Building Models with IEC 61850 and Jneopallium

User Manual

Substation automation · read-only by construction · MMS + report control blocks

Version: 1.0-SNAPSHOT

License: BSD 3-Clause

Author: Dmytro Rakovskyi

# 1. Introduction

[IEC 61850](https://www.iec.ch/) is the international standard for electrical substation automation. Its scope is the data model and protocol stack used by Intelligent Electronic Devices (IEDs) — the protection relays, bay controllers, merging units, and bay-level computers inside a high-voltage substation — to communicate with each other and with the station-level SCADA. Every modern substation built in the last fifteen years speaks 61850; legacy substations are migrating to it as part of refurbishment cycles.

The IEC 61850 bridge connects Jneopallium to substation IEDs. It speaks the Manufacturing Message Specification (MMS) over TCP, reads functional-constraint Data Attribute (DA) paths via direct reads, subscribes to Report Control Blocks (RCBs) for event-driven updates, and parses the IED's Substation Configuration Language (SCL) file to validate paths at startup. The decoded values become typed Jneopallium signals: MeasurementSignal for MMXU-style measurements (voltages, currents, powers), InterlockSignal for XCBR / XSWI status (breakers and switches — state-only, never used to trip anything), and AlarmSignal for protection events from RCB reports (PIOC overcurrent, PDIS distance, PTOC time-overcurrent, etc.).

The bridge is read-only by construction. This is the strictest safety posture in the entire bridge directory — even stricter than FHIR (which has structural defences against writes) and DICOM (which has no aggregator class but does have a write-capable transport surface in principle). The IEC 61850 bridge has all three: no aggregator class anywhere in the package, an MMS transport seam with only readDa() and subscribeReport() methods (no write methods exist at all), and a config-load rejection of any writes: block with a clear message pointing to the spec sections that forbid it.

Why this matters: substation control — opening or closing a breaker, raising or lowering a tap-changer, blocking or releasing a protection element — is a SIL-classified function. Substation control writes go through certified RTUs and protection relays, not through general-purpose computing. The IEC 61850 standard itself reserves control operations for select-before-operate sequences that include cryptographic auth, deadman timers, and operator confirmation steps. A bridge that put an AI on the write side of that would violate every safety and certification regime that applies to high-voltage power infrastructure. So the bridge structurally cannot write. If a future deployment requires AI-assisted control, that's a separately scoped iec61850-control bridge with its own safety case and certification — not a flag flip on this one.

This manual explains how to install the dependency, configure the bridge against an IED (vendor IED, simulator, or test substation), parse SCL files, design MMXU read bindings and RCB subscriptions, validate end to end, and understand the regulatory posture. It assumes a Java engineer who knows Maven, has read the universal bridge framework (00-FRAMEWORK.md), and has at least basic familiarity with IEC 61850 concepts (the IED → AccessPoint → Server → LDevice → LN → DO → DA hierarchy, Logical Node classes like MMXU and XCBR, Report Control Blocks).

# 2. Six rules you must internalise before writing any code

The universal six from 00-FRAMEWORK.md §0, specialised for IEC 61850. The first four are stricter than any other bridge in the directory.

- No write to an IED from anywhere. The bridge has no aggregator class. The transport seam has no write methods. writes: in YAML fails to load. Three independent structural defences. There is no environment variable, no flag, no test-mode bypass.

- Interlocks are observable, not actuated. XCBR / XSWI status fields produce InterlockSignal values, but the tripped field is always false — the bridge produces a state view, not a control action. Neurons reading these signals can incorporate substation state into their reasoning; they cannot change that state.

- Operator override does not apply. The bridge writes no regulatory control. OperatorOverrideSignal is ignored.

- Every poll, every RCB report, and every SCL parse produces an audit record. Records cover successful DA reads, MMS association failures, report subscriptions, SCL validation failures, and reconnects. Audits are local JSONL only — substation audit infrastructure (sequence-of-events recorders, IEC 62351 syslog) is operator-managed.

- Quality propagates from MMS. IEC 61850 carries explicit quality codes on every DA value (the q attribute — good / invalid / questionable / overflow / etc.). The mapper translates validity=good → Quality.GOOD, validity=invalid → Quality.BAD, validity=questionable → Quality.UNCERTAIN, with overflow and out-of-range also downgrading to UNCERTAIN. The framework Quality.GOOD default is never used — every signal carries a vendor-derived quality.

- Wall-clock timestamps come from the IED. Every DA has a t (timestamp) attribute populated by the IED's own clock — typically PTP-synchronized in modern substations. The mapper honours this. System.currentTimeMillis() is only used when an MMS response arrives without a timestamp attribute (rare, indicates an IED configuration issue).

# 3. Prerequisites

- JDK 17 or later. The bridge uses Java records, java.io, and javax.xml.stream (StAX) for SCL parsing.

- Maven 3.9 or later.

- Network access to one or more IEDs on the substation network. MMS uses TCP port 102 by convention; ensure that port is reachable from the bridge host.

- An SCL file (.icd, .iid, .cid, or .scd) per IED. The substation's configuration management team owns these; ask for the file for each IED you intend to bind.

- The bridge core compiles without any IEC 61850 client library. Production deployments add an MMS adapter (org.openmuc:iec61850bean is the standard Java option; the JNI bindings of libiec61850 are an alternative) in the deployment module and supply an Iec61850MmsClient adapter.

- For test scenarios: the InMemoryIec61850MmsClient ships in src/test/java and accepts pre-loaded DA values plus simulated report subscriptions. Useful for unit and integration tests.

- For operational deployment in a real substation: cyber-security approval per IEC 62443 and IEC 62351, network isolation per the substation's defense-in-depth zone model, and a maintenance-of-changes process for any YAML or topology changes. None of these is a software dependency, but they are non-optional.

# 4. Adding Jneopallium to your project

The IEC 61850 bridge ships in the same worker artifact as the rest of Jneopallium:

<repositories> <repository> <id>gitlab-jneopallium</id> <url>https://gitlab.com/api/v4/projects/44434192/packages/maven</url> </repository> </repositories> <dependencies> <dependency> <groupId>com.rakovpublic.jneopallium</groupId> <artifactId>worker</artifactId> <version>1.0-SNAPSHOT</version> </dependency> </dependencies>

No IEC 61850 client library is required by the bridge core. For production deployments, add iec61850bean in your deployment module:

<dependency> <groupId>org.openmuc</groupId> <artifactId>iec61850bean</artifactId> <version>1.7.0</version> <scope>runtime</scope> </dependency>

The bridge stays unaware of iec61850bean — it only uses the read-only methods on the Iec61850MmsClient interface. Your deployment supplies an IedBeanMmsClient adapter that delegates to iec61850bean's ClientAssociation for reads and BasicDataAttribute reads.

# 5. Architecture

The bridge introduces eleven classes under worker.bridge.iec61850:

┌──────────────────────────────────┐ MMS reads (DA path → value) │ Substation │ ──────────────────────────────┐ │ IED-1 (relay) │ │ │ LD0/MMXU1.PhV.phsA.cVal │ │ │ LD0/XCBR1.Pos.stVal │ │ │ LD0/PIOC1.Op.general │ │ │ │ MMS reports │ │ IED-2 (bay controller) │ (Report Control Block │ │ IED-3 (merging unit) │ subscriptions) │ │ │ ──────────────────────────────│ │ SCL file: substation.scd │ │ │ (parsed at startup only) │ │ └──────────────────────────────────┘ │ ▼ ┌──────────────────────────────────────┐ │ Iec61850ClientService │ │ • owns the MMS client per IED │ │ • per-binding poll scheduler │ │ • SCL-validated DA bindings │ │ • report-subscription lifecycle │ │ • per-binding signal queues │ └────────────┬──────────────────────────┘ │ ┌────────────┼─────────────────┐ │ │ │ ┌───────────────▼──┐ ┌───────▼─────────────────▼─┐ │ Iec61850 │ │ Iec61850 │ │ MeasurementInput │ │ EventInput │ │ (IInitInput → │ │ (IInitInput → │ │ Measurement / │ │ Alarm) │ │ Status) │ │ │ └──────────────────┘ └───────────────────────────┘ ▼ [Standard Jneopallium pipeline] NO aggregator class. NO writeProperty(). The bridge produces signals only.

Components:

| Class | Role |
| --- | --- |
| Iec61850BridgeConfig | YAML record (immutable). Rejects writes: block at config load with the spec reference in the message. |
| Iec61850BridgeConfigLoader | Jackson YAML loader. FAIL_ON_UNKNOWN_PROPERTIES = true. |
| Iec61850MmsClient | Test-seam interface. isReady / readDa / subscribeReport / close. No write methods exist. |
| InMemoryIec61850MmsClient | Test client preloaded with DA values and synthetic report payloads. |
| SclParser | Reads .icd / .scd files. Surfaces IED → AccessPoint → Server → LDevice → LN → DO → DA hierarchy. Validates configured DA paths at startup. |
| Iec61850DaBinding | Resolved binding identity at runtime. |
| Iec61850SignalMapper | Pure functions. Maps DA values + quality codes → MeasurementSignal / InterlockSignal / AlarmSignal. Translates IEC 61850 quality to framework Quality. |
| Iec61850ClientService | Owns one MMS client per IED, the per-binding scheduler, the SCL parser output, the signal queues, and the audit channel. AutoCloseable. |
| Iec61850MeasurementInput | IInitInput. Drains MEASUREMENT and STATUS bindings. |
| Iec61850EventInput | IInitInput. Drains ALARM bindings (subscribed to via RCBs). |
| Iec61850AuditOutput | Local JSONL append-only audit. |

Notably absent: no `OutputAggregator` class anywhere in the package. The bridge cannot be wired to an output. A code path that calls worker.registerOutputAggregator(...) from this package fails to compile because there's nothing to register. The structural read-only design lives at the package level.

# 6. The three structural defences

The IEC 61850 bridge has the strictest safety posture in the directory. Three layered guards together make this bridge incapable of writing to an IED:

Defence 1 — no aggregator class. The worker.bridge.iec61850 package contains zero IOutputAggregator implementations. A worker.registerOutputAggregator(new Iec61850OutputAggregator()) line wouldn't compile because the class doesn't exist. A future maintainer wanting to add write authority would have to create the class first, which would be a substantial diff visible in any code review.

Defence 2 — transport interface read-only. Iec61850MmsClient exposes only isReady, readDa, subscribeReport, and close. There is no writeDa, no controlSelect, no controlOperate, no method that takes a write parameter. The JavaDoc on the interface is explicit: "No method writes a Data Attribute, issues a select-before-operate, or controls a breaker — substation control writes are a SIL-classified function that lives on certified RTUs and protection relays. A production implementation backed by org.openmuc:iec61850bean or the JNI bindings of libiec61850 provides only the methods on this surface; an attempt to add a write method here is a build break."

Defence 3 — `writes:` rejected at config load. Iec61850BridgeConfig.create() declares a @JsonProperty("writes") Object writes parameter — declared so Jackson with FAIL_ON_UNKNOWN_PROPERTIES = true doesn't reject it silently. The factory body checks for non-null and throws IllegalArgumentException with the message:

> "IEC 61850 bridge: 'writes:' block is not permitted — the bridge ceiling is READ-ONLY (11-IEC61850.md §0, §3, §6). Control surface is a separate bridge ('iec61850-control') that must be certified separately. Remove the writes section."

A YAML accidentally including a writes: section is caught at load with the message naming the spec sections that forbid it and pointing the operator at the correct next step.

The defences are layered and independent. Defence 1 prevents the class from existing. Defence 2 prevents the call from compiling even if a class existed. Defence 3 prevents the configuration from loading even if both other defences were somehow bypassed. There is no flag, no environment variable, no test-mode bypass that changes any of this.

# 7. Configuration

Configuration is YAML, loaded once at startup through Iec61850BridgeConfigLoader.load(Path). Hot-reload is not supported. The loader sets FAIL_ON_UNKNOWN_PROPERTIES = true. There is no `writes:` section, and including one fails the load.

## 7.1 Schema

The configuration has five top-level keys.

- ied — list of IEDs, each with an id, host, port (default MMS port 102), SCL file path, and optional default Report Control Block.

- reads — list of direct DA read bindings.

- events — list of RCB subscription bindings.

- audit — local JSONL audit file path.

- tickInterval — worker tick cadence. Default PT1S.

## 7.2 Minimal example — single-IED smoke test

The smallest useful configuration. One IED, two read bindings (one MMXU measurement, one XCBR status), no events, no writes. Suitable as a first integration check against a vendor simulator or against InMemoryIec61850MmsClient in tests.

ied: - id: "IED-1" host: "192.168.1.10" port: 102 sclFile: "/etc/jneopallium/scl/IED-1.icd" reads: - bindingId: "VL1-PHV-A" iedId: "IED-1" daPath: "LD0/MMXU1.PhV.phsA.cVal.mag.f" signalTag: "SUB.VL1.PHV.A" targetSignal: MEASUREMENT - bindingId: "CB1-POS" iedId: "IED-1" daPath: "LD0/XCBR1.Pos.stVal" signalTag: "SUB.CB1.POS" targetSignal: STATUS events: [] audit: localAuditFile: "/var/log/jneopallium/iec61850-audit.jsonl" tickInterval: "PT1S"

## 7.3 Production-like example — multi-IED with report subscriptions

A more substantial config: three IEDs (a protection relay, a bay controller, a merging unit), MMXU measurements from each, breaker and switch statuses, and Report Control Block subscriptions for protection events. No writes: — the bridge cannot have one.

ied: - id: "RELAY-VL1" host: "10.10.1.21" port: 102 sclFile: "/etc/jneopallium/scl/RELAY-VL1.icd" reportControlBlock: "LD0/LLN0$RP$urcb01" - id: "BAY-CTRL-VL1" host: "10.10.1.22" port: 102 sclFile: "/etc/jneopallium/scl/BAY-CTRL-VL1.icd" - id: "MU-VL1" host: "10.10.1.23" port: 102 sclFile: "/etc/jneopallium/scl/MU-VL1.icd" reads: - bindingId: "VL1-V-A" iedId: "MU-VL1" daPath: "LD0/MMXU1.PhV.phsA.cVal.mag.f" signalTag: "SUB.VL1.V.A" - bindingId: "VL1-V-B" iedId: "MU-VL1" daPath: "LD0/MMXU1.PhV.phsB.cVal.mag.f" signalTag: "SUB.VL1.V.B" - bindingId: "VL1-V-C" iedId: "MU-VL1" daPath: "LD0/MMXU1.PhV.phsC.cVal.mag.f" signalTag: "SUB.VL1.V.C" - bindingId: "VL1-I-A" iedId: "MU-VL1" daPath: "LD0/MMXU1.A.phsA.cVal.mag.f" signalTag: "SUB.VL1.I.A" - bindingId: "VL1-FREQ" iedId: "MU-VL1" daPath: "LD0/MMXU1.Hz.mag.f" signalTag: "SUB.VL1.FREQ" - bindingId: "CB1-POS" iedId: "BAY-CTRL-VL1" daPath: "LD0/XCBR1.Pos.stVal" signalTag: "SUB.CB1.POS" targetSignal: STATUS - bindingId: "DS1-POS" iedId: "BAY-CTRL-VL1" daPath: "LD0/XSWI1.Pos.stVal" signalTag: "SUB.DS1.POS" targetSignal: STATUS events: - bindingId: "RELAY-VL1-REPORTS" iedId: "RELAY-VL1" reportControlBlock: "LD0/LLN0$RP$urcb01" targetSignal: "ALARM" severityMap: PIOC: "URGENT" # instantaneous overcurrent — protection trip imminent PDIS: "URGENT" # distance protection PTOC: "HIGH" # time overcurrent PSCH: "HIGH" # protection scheme communication PTRC: "HIGH" # trip conditioning RREC: "LOW" # autoreclose audit: localAuditFile: "/var/log/jneopallium/iec61850-audit.jsonl" tickInterval: "PT0.5S"

## 7.4 Field reference

ied[].id is the IED identifier as it appears in the SCL file's <IED name="..."> element. The bridge validates this at startup against the parsed SCL.

ied[].host is the IED's IP address or hostname on the substation process bus or station bus. Production substations have dedicated VLANs for this traffic.

ied[].port defaults to 102, the MMS well-known TCP port. Change only if your IED uses a non-standard port (rare; some legacy gateways do).

ied[].sclFile is the local path to the IED's SCL file. Supported file types: .icd (IED Capability Description), .iid (Instantiated IED Description), .cid (Configured IED Description), .scd (Substation Configuration Description). The parser only uses the IED → AccessPoint → Server → LDevice → LN → DO → DA skeleton — vendor-specific attributes are ignored. The bridge fails fast at startup if the SCL file is missing or unparseable.

ied[].reportControlBlock is an optional default RCB used by events: entries that don't specify one. The format is LD/LN$variant$rcbName per IEC 61850 syntax: typically LD0/LLN0$RP$urcb01 for the first un-buffered report or LD0/LLN0$BR$brcb01 for the first buffered report.

reads[].iedId references an entry in the ied: list. References to undefined IED ids fail at config load.

reads[].daPath is the IEC 61850 functional-constraint path. The format is LD/LN.DO.DA[.DA…]: logical device, logical node, data object, data attribute(s). Example: LD0/MMXU1.PhV.phsA.cVal.mag.f reads the floating-point magnitude of phase A voltage from the first MMXU logical node in LD0.

reads[].targetSignal is MEASUREMENT, STATUS, or ALARM. When omitted, the mapper infers from the LN prefix in the path: XCBR/XSWI → STATUS, everything else defaults to MEASUREMENT.

events[].reportControlBlock is the per-event RCB to subscribe to. Falls back to the IED's default RCB if omitted.

events[].severityMap maps Logical Node class prefix → AlarmPriority (URGENT, HIGH, LOW, JOURNAL). The mapper looks up the LN class from the SCL (e.g. a report entry from LD0/PIOC2$ST$Op has LN class PIOC) and emits the AlarmSignal with the mapped priority. LN class prefixes not in the map default to LOW.

tickInterval is the worker tick cadence. The bridge's per-binding scheduler reads at most once per tick per binding — set this to a value compatible with your IED's reporting capabilities and SCADA polling conventions.

# 8. Wiring the Java side

The bootstrap registers inputs only. There is no aggregator to register.

package com.example.substation; import com.rakovpublic.jneuropallium.worker.bridge.common.AbstractBridgeAuditOutput; import com.rakovpublic.jneuropallium.worker.bridge.iec61850.Iec61850AuditOutput; import com.rakovpublic.jneuropallium.worker.bridge.iec61850.Iec61850BridgeConfig; import com.rakovpublic.jneuropallium.worker.bridge.iec61850.Iec61850BridgeConfigLoader; import com.rakovpublic.jneuropallium.worker.bridge.iec61850.Iec61850ClientService; import com.rakovpublic.jneuropallium.worker.bridge.iec61850.Iec61850EventInput; import com.rakovpublic.jneuropallium.worker.bridge.iec61850.Iec61850MeasurementInput; import com.rakovpublic.jneuropallium.worker.bridge.iec61850.Iec61850MmsClient; import com.rakovpublic.jneuropallium.worker.bridge.iec61850.Iec61850SignalMapper; import com.rakovpublic.jneuropallium.worker.bridge.iec61850.SclParser; import java.nio.file.Path; public final class Iec61850Bootstrap { public static void main(String[] args) throws Exception { // 1. Load YAML. A 'writes:' block here fails the load. Iec61850BridgeConfig cfg = Iec61850BridgeConfigLoader.load( Path.of("iec61850-bridge.yml")); // 2. Parse SCL files. Fail fast if any are missing or malformed. SclParser.Tree[] sclTrees = cfg.ied().stream() .map(ied -> SclParser.parse(Path.of(ied.sclFile()))) .toArray(SclParser.Tree[]::new); // 3. Open the audit sink. try (AbstractBridgeAuditOutput audit = new Iec61850AuditOutput( Path.of(cfg.audit().localAuditFile()))) { // 4. Build the MMS client. Production: a real iec61850bean // or libiec61850-backed adapter. Tests: InMemoryIec61850MmsClient. // The client interface has NO write methods. try (Iec61850MmsClient mms = new IedBeanMmsClient(cfg)) { // 5. Build the signal mapper and the client service. Iec61850SignalMapper mapper = new Iec61850SignalMapper(cfg, sclTrees); Iec61850ClientService svc = new Iec61850ClientService( cfg, mms, mapper, audit); // 6. Start: open MMS associations to all IEDs, subscribe // to all configured RCBs, schedule polls for `reads`. svc.start(); try { // 7. Build the inputs. Two by signal family. Iec61850MeasurementInput meas = new Iec61850MeasurementInput( "iec61850-meas", svc); Iec61850EventInput events = new Iec61850EventInput( "iec61850-events", svc); // 8. Register with the worker. // // NOTE: there is no aggregator to register. The bridge // has no write surface. Neurons consuming IEC 61850 // signals make decisions that flow through OTHER // bridges (the FHIR-style advisory file, MQTT // advisory topics, etc.), never back to an IED. worker.registerInput(meas); worker.registerInput(events); worker.run(); } finally { svc.close(); } } } } }

Three implementation notes worth highlighting. Exactly one input class registration per signal family, no aggregator. The bootstrap registers Iec61850MeasurementInput (which produces MeasurementSignal and InterlockSignal) and Iec61850EventInput (which produces AlarmSignal). Both flow into the standard Jneopallium pipeline. Whatever the neurons decide, they cannot push back through this bridge — they push through the FHIR advisory file, an MQTT advisory topic, or whatever other egress bridge the deployment has wired. SCL parsing fails fast at startup. A missing or malformed SCL file aborts the bootstrap with a clear error before any MMS connection is attempted. This is intentional: a substation deployment without validated path topology is more dangerous than no deployment at all. The MMS client is `AutoCloseable`. Closing it releases the MMS association on each IED cleanly. Failure to close leaves orphan associations that the IED eventually times out — harmless but flags monitoring.

# 9. Modeling guidance

## 9.1 What to read

For a substation-monitoring deployment, a typical binding set:

- Three-phase voltage and current from each MMXU instance — phases A/B/C, voltage and current magnitude. Six bindings per measurement point.

- Frequency from the MMXU Hz.mag.f attribute. One binding.

- Active and reactive power from MMXU TotW.mag.f and TotVAr.mag.f. Two bindings per measurement point.

- Breaker positions from XCBR Pos.stVal. One STATUS binding per breaker.

- Switch positions from XSWI Pos.stVal. One STATUS binding per disconnector or earthing switch.

- Protection trips via RCB subscription on the relay's main RCB. One event binding per relay.

For a wide-area-monitoring deployment, scale this per substation. The bridge handles dozens of IEDs comfortably with tickInterval: PT0.5S; very high-frequency sampled-value (SV) streams are a different protocol layer not in the bridge's scope.

## 9.2 The targetSignal mapping table

The bridge maps each binding kind to a Jneopallium signal class:

| `targetSignal` | Signal class produced | Source DA path pattern |
| --- | --- | --- |
| MEASUREMENT | MeasurementSignal | MMXU<n>.<measurement>.<phase>.cVal.mag.f (and similar) |
| STATUS | InterlockSignal (state-only, never tripped) | XCBR<n>.Pos.stVal, XSWI<n>.Pos.stVal |
| ALARM | AlarmSignal | RCB subscription; severity from severityMap per LN class |

The signal carries the DA path, the IED id, the value, the IEC 61850 quality (translated to framework Quality), and the IED-side timestamp.

## 9.3 Reading SCL: what the parser uses

The SclParser extracts a minimal subset of the SCL XML:

- <IED name="..."> — IED identifiers

- <AccessPoint name="..."> → <Server> → <LDevice inst="..."> — logical device names

- <LN class="..." lnType="..." inst="..." prefix="..."> — logical node instances

- <DO name="..."> (via LNType resolution) — data objects

- <DA name="..."> (via DOType resolution) — data attributes

The parser ignores everything else: vendor-specific attributes, data types, addresses, services, communication parameters. This stability matters because SCL dialects drift between vendors (ABB, Schneider, SEL, Siemens, GE). The narrow surface the parser uses is stable across all of them.

Validation at startup: every configured reads[].daPath must resolve to a real DA in the SCL tree. A path referring to a non-existent LN or DA fails the bootstrap with a message naming the binding and the path component that's missing.

## 9.4 What signals to bind on event reports

Protection relay RCBs deliver event records for protection-element operation. Typical entries:

- PIOC<n>$ST$Op.general — instantaneous overcurrent trip

- PDIS<n>$ST$Op.general — distance protection trip

- PTOC<n>$ST$Op.general — time-overcurrent trip

- PSCH<n>$ST$Op.general — protection scheme communication signal

- PTRC<n>$ST$Op.general — trip conditioning output

- RREC<n>$ST$Op.general — autoreclose operation

Map these in severityMap per their criticality. URGENT for direct trip indications (PIOC, PDIS), HIGH for delayed or conditioning trips (PTOC, PSCH, PTRC), LOW for autoreclose and other auxiliary indications (RREC). The bridge emits AlarmSignal per report data set entry with the mapped priority.

## 9.5 Where AI decisions go (since not back to the IED)

Substation-AI decisions from neurons reading these signals can:

- Write to a FHIR-style advisory file that the substation operator's HMI reads. The deployment runs both this bridge (read) and an MQTT or file-based advisory egress.

- Flag to the SCADA via a separate channel — typically an OPC UA or MQTT bridge writing to a "recommendation" namespace that the SCADA displays alongside real values.

- Trigger a maintenance work order through whatever ticketing system the substation uses, via the appropriate bridge (LTI, Kafka, etc.).

What never happens: AI decisions writing back through IEC 61850. The bridge has no write surface. If a future deployment needs AI-assisted control, that's a separately certified iec61850-control bridge with its own safety case — not this one.

# 10. The (absent) egress algorithm

Unlike every other bridge in the directory, IEC 61850 has no egress algorithm chapter to document. There's nothing to clamp, no rate limit to apply, no interlock fail-safe to write, no SHADOW/ADVISORY/AUTONOMOUS ladder — because there's no write path. The bridge produces signals; the worker's neurons reason about them; the resulting decisions flow through other bridges entirely.

This negative space is the substation safety contract in code form. The IEC 61850 standard reserves control writes for select-before-operate sequences executed by certified equipment with cryptographic auth, deadman timers, and operator confirmation. An AI bypassing that would violate the safety case of the entire substation. So the bridge structurally cannot bypass it.

# 11. Audit and transparency

The bridge writes one JSONL record per decision to the local audit:

{ "ts": 1740000000000, "run": 12345, "bridge": "iec61850", "verdict": "APPLIED", "tag": "SUB.VL1.V.A", "iedId": "MU-VL1", "daPath": "LD0/MMXU1.PhV.phsA.cVal.mag.f", "value": 230.5, "unit": "V", "iecQuality": "good", "iecTimestamp": 1740000000000, "reason": "DA_READ_OK", "safetyMode": "READ_ONLY" }

Records you will see:

| `verdict` | `reason` | Triggered by |
| --- | --- | --- |
| APPLIED | DA_READ_OK | DA value read successfully. |
| APPLIED | RCB_REPORT_RECEIVED | Report received on subscribed RCB. |
| APPLIED | BRIDGE_RECONNECTED | MMS association re-established. |
| APPLIED | SCL_VALIDATED | SCL file parsed and all configured paths resolved at startup. |
| REJECTED | QUALITY_INVALID | DA value carries validity=invalid; no signal produced. |
| REJECTED | QUALITY_QUESTIONABLE | DA value carries validity=questionable; signal still produced but with Quality.UNCERTAIN. |
| FAILED | MMS_ASSOC_FAILED | Cannot open MMS association to IED. |
| FAILED | MMS_READ_ERROR:<detail> | Read failed at the transport. |
| FAILED | RCB_SUBSCRIBE_FAILED | Cannot subscribe to configured RCB. |
| FAILED | SCL_PARSE_ERROR:<file> | SCL file missing or malformed. |
| FAILED | SCL_PATH_NOT_FOUND | Configured daPath doesn't resolve in SCL. |

There is no INTERLOCK_TRIP row — the bridge has no aggregator, so it produces no interlock decisions of its own. (InterlockSignals with tripped=false are produced for breaker status, but those represent state, not trip actions.) There is no CLAMPED_* row — no values are clamped because no values are written.

The audit file is local. No mirror to syslog, MQTT, or SIEM. The substation's existing sequence-of-events recorder and IEC 62351 audit infrastructure remain the operator's responsibility.

# 12. Operating procedures

## 12.1 Smoke test with in-memory MMS client

For development and CI without real IEDs:

- Construct new InMemoryIec61850MmsClient().

- Pre-load with DA values via the client's helper methods.

- Provide a small SCL XML in a test resource matching the configured paths.

- Tick the worker. The bridge sees the in-memory values as if they were real.

This is what Iec61850BridgeIntegrationTest does for every scenario.

## 12.2 Smoke test against a real IED

Against a vendor relay on a lab network:

- Get the SCL file from the relay's configuration tool (ABB PCM600, Schneider SFT2841, SEL AcSELerator Architect, Siemens Digsi, etc.).

- Save §7.2 minimal config to iec61850-bridge.yml. Point sclFile at the file from step 1.

- Run Iec61850Bootstrap (§8) with a real IedBeanMmsClient-backed setup.

- Within the first tick the bridge opens an MMS association and reads the configured DA paths.

- Inspect the audit JSONL: SCL_VALIDATED, DA_READ_OK records appear.

## 12.3 Verifying the structural read-only guarantee

A useful audit step:

- Read Iec61850MmsClient.java. Confirm the methods are exactly isReady, readDa, subscribeReport, close. No write methods.

- grep -r "OutputAggregator" worker/src/main/java/com/rakovpublic/jneuropallium/worker/bridge/iec61850/ — no hits.

- Test: add a writes: [] block to YAML and try to load. Loader fails with the message naming 11-IEC61850.md §0, §3, §6 and pointing at the separate iec61850-control bridge as the right path for control.

Three structural defences, three places to audit. If any have changed, the bridge's safety posture has changed and the change needs scrutiny.

## 12.4 Diagnosing report-subscription failures

RCB subscription issues are the most common operational pain point. Symptoms in the audit JSONL:

- RCB_SUBSCRIBE_FAILED reason=BUFFER_TIME_INVALID — the IED rejected the requested buffer time. Adjust per the IED's published RCB configuration.

- RCB_SUBSCRIBE_FAILED reason=RPT_ENA_NOT_PERMITTED — the report is currently in use by another client. Check the substation's MMS client inventory; the bridge cannot share a single RCB with another client.

- RCB_SUBSCRIBE_FAILED reason=DATSET_NOT_FOUND — the RCB references a dataset that doesn't exist in the IED. Check the SCL: did a recent configuration change break the RCB?

Each of these is an IED-side configuration question, not a bridge bug. Coordinate with the substation engineer who owns the IED.

## 12.5 Reconnection after MMS association loss

The bridge handles association loss with exponential backoff:

- MMS association breaks (network blip, IED reboot, etc.).

- The next readDa() returns IOException or isReady() == false.

- The bridge logs FAILED reason=MMS_ASSOC_FAILED.

- Backoff loop attempts to reconnect: 1 s, 2 s, 4 s, 8 s, capped at 60 s.

- On successful reconnect, the bridge re-establishes any RCB subscriptions and resumes polls.

- Audit emits APPLIED reason=BRIDGE_RECONNECTED.

Long outages eventually saturate backoff. Restart the bridge if the audit shows continuous reconnection attempts over many minutes.

# 13. Cybersecurity posture

IEC 61850 deployments are governed by IEC 62443 (industrial automation security) and IEC 62351 (power system security). Both are operator concerns — the bridge does not implement them — but the bridge's design respects them:

- Bridge runs in the operator's defense-in-depth zone. The substation network architecture isolates MMS traffic to specific zones; the bridge runs in a zone compatible with reading those MMS streams. Operator-defined.

- No control writes from the bridge. As §6 documents. The structural read-only design satisfies the IEC 62443 SL (security level) intent without needing additional access control on the bridge side — the bridge can't issue a control even if compromised.

- MMS authentication and encryption are operator concerns. IEC 62351-4 specifies TLS for MMS. The bridge's Iec61850MmsClient interface is transport-agnostic; production adapters speak TLS-protected MMS where the substation operator has deployed that.

- Audit log retention is operator-managed. The bridge produces JSONL; the operator's log aggregation infrastructure (SIEM, sequence-of-events recorder) consumes it.

- No external network egress from the bridge. The bridge connects only to configured IEDs and writes to local files. No telemetry to cloud, no auto-update, no remote support phone-home.

# 14. Limitations and future work

- No write to IEDs, ever. Structural and intentional. AI-assisted control needs a separate iec61850-control bridge with its own safety case.

- No sampled values (SV). IEC 61850-9-2 sampled-value streams (high-frequency current and voltage samples at 4000+ Hz) are out of scope. The bridge consumes MMS data only.

- No GOOSE messaging. Generic Object-Oriented Substation Event messages are a peer-to-peer protocol used between IEDs at the protection layer; they are not for client consumption and the bridge does not subscribe to them.

- One MMS client per IED. Multi-association per IED is not supported. For high-throughput requirements, run multiple bridge instances each scoped to subsets of IEDs.

- SCL parser is read-only. SCL editing is operator tooling; the bridge consumes SCL but never modifies it.

- No 61850-90-x extensions. The bridge implements the core 61850-7-x data model and 61850-8-1 MMS mapping. Extensions like 61850-90-2 (wind farms), 61850-90-7 (DER), 61850-90-12 (WAN considerations) are not specifically supported but generally work if the IED reports through standard 61850-7-x objects.

# 15. Regulatory posture

| Aspect | Posture |
| --- | --- |
| Safety ceiling | READ-ONLY by construction. Three structural defences: no aggregator class, no transport write methods, writes: rejected at config load. |
| Default per-binding mode | N/A — there are no write bindings. |
| Forbidden write surfaces | All control operations: select, operate, set, write. None exposed on the transport interface. |
| writes: block | Rejected at config load with a message pointing to 11-IEC61850.md §0, §3, §6 and naming the separate iec61850-control bridge. |
| Interlock authority | None. Breaker / switch status is observable as InterlockSignal(tripped=false); the bridge never trips anything. |
| Operator override | Not applicable. |
| Audit | Local JSONL. No mirror. Operator's IEC 62351 audit infrastructure remains the source of truth for substation events. |
| Quality | IEC 61850 native quality codes translate to framework Quality.GOOD / UNCERTAIN / BAD. |
| MoC | Hot-reload not supported. YAML changes follow substation-side maintenance-of-changes procedures. |
| Cybersecurity | IEC 62443 / IEC 62351 are operator responsibility; the bridge's structural read-only design eliminates entire categories of attack surface. |

The bridge is appropriate for any deployment where AI reasoning over substation telemetry is needed but writes to substation equipment are categorically off-limits. The structural defences make this guarantee robust against careless future maintenance.

# 16. References

- 11-IEC61850.md — the bridge specification.

- 00-FRAMEWORK.md — the universal bridge contract.

- docs/iec61850-bridge.md — domain-context companion in the repo.

- IEC 61850 — https://www.iec.ch/. Substation Automation Standard.

- IEC 62443 — https://www.iec.ch/cyber-security. Industrial automation security.

- IEC 62351 — https://webstore.iec.ch/publication/6913. Power system security.

- iec61850bean — https://www.openmuc.org/iec-61850/. The standard Java IEC 61850 client library.

- libiec61850 — https://libiec61850.com/. C IEC 61850 library, accessible via JNI.

- SCL Schema — IEC 61850-6. Substation Configuration Description Language.

- Common Information Model (CIM) — IEC 61970/61968. Related power-system data model (not used by this bridge but often co-deployed).

- Rakovskyi, D. (2024). Framework for Natural Neuron Network Modeling: The Jneopallium Approach. IJSR 13(7).